## Strobe Coverage
Strobe Coverage Calculator
System Sensor is pleased to provide this Strobe Coverage Calculator, formerly known as Equivalent Facilitation Calculator. The calculator was programmed to assist you in the design of audible/visible notification device circuits.
This calculator uses data provided by the user to perform the calculations described in NFPA 72-, which permits the use of a performance-based alternative in lieu of tables for spacing ceiling mounted audible/visible devices. These calculations are described in NFPA 72 and are to be provided to the authority having jurisdiction.
To calculate performance-based strobe coverage, the inverse square law is used to calculate the illumination at each of the angles in the horizontal and vertical planes per ANSI/UL 1971, Standard for Signaling Devices for the Hearing Impaired, and the effect of polar distribution is included using the minimum percentages in ANSI/UL 1971 or actual test results recorded by the Listing organization.
The calculated illumination is required to be at least 0.0375 lumens/ft2 at any point within the covered area. The calculation points are in the horizontal and vertical planes in 5 degree increments per UL 1971. For the effect of polar distribution (rated candela at each angle), the ANSI/UL 1971 minimum percentages are used for the calculations. ANSI/UL 1971 does not provide ratings for each angle based on actual test results."
There are no express or implied warranties of any kind with this calculator. System Sensor does not provide any design or engineering services. Users of this calculator are solely responsible for their own selection and use of products based upon information contained in this calculator and any calculations from this calculator. System Sensor shall have no liability.
circle radius
25
| Candela | 75
[7 empty] | 15 |  | 0.9
| Square Room Size (ft)*: |  |  | Ceiling Height (ft): | 15 |  | 30 |  | 0.75
|  | 50 |  |  |  |  | 75
| *Input length of the longest wall | [5 empty] | 95 |  | 0.55
| ceiling height | [5 empty] | 110 |  | 0.45
Inscribed equivalent facilitation | [6 empty] | 115 |  | 0.4
Angle | U.L Required Candela | Distance | Lumens/ft² |  |  |  | 135 |  | 0.35
0 | 75 | 15 | 0 |  |  | 0 | 150 |  | 0.3
5 | 67.5 | 15.0573 | 0.29772 |  |  | 1.3123 | 177 |  | 0.25
10 | 67.5 | 15.2314 | 0.29095 |  |  | 2.6449 | 185
15 | 67.5 | 15.5291 | 0.2799 |  |  | 4.0192
20 | 67.5 | 15.9627 | 0.26491 |  |  | 5.4596
25 | 67.5 | 16.5507 | 0.24642 |  |  | 6.9946
30 | 56.25 | 17.3205 | 0.1875 |  |  | 6.9946
35 | 56.25 | 18.3116 | 0.16775 |  |  | 10.5031
40 | 56.25 | 19.5811 | 0.14671 |  |  | 12.5865
45 | 56.25 | 21.2132 | 0.125 |  |  | 15
50 | 41.25 | 23.3359 | 0.075749 |  |  | 17.8763
55 | 33.75 | 26.1517 | 0.049348 |  |  | 21.4222
60 | 30 | 28.8675 | 0.036 |  |  | 25.9808
65 | 26.25 | 27.5844 | 0.034499 |  |  | 32.1676
70 | 26.25 | 26.6044 | 0.037087 |  |  | 41.2122
75 | 22.5 | 25.8819 | 0.033588 |  |  | 55.9808
80 | 22.5 | 25.3857 | 0.034914 |  |  | 85.0692
85 | 18.75 | 25.0955 | 0.029772 |  |  | 171.4508
90 | 18.75 | 25 | 0.03 |  |  | 2.4487e+17
Assumptions:
1. Minimum calculated illumination requirement of 0.0375 lm/ft2.
2. Square rooms with ceiling mounted strobes in the center of the ceiling.
3. Illumination is calculated for two perpendicular planes with brightest profile.